## Slide 1: Preventative Maintenance For Water Treatment Systems
Presented by:

## Slide 2: Preventative Maintenance
PM will:
Prolong the life of equipment
Provide more efficiently operating systems
Minimize emergency maintenance calls
Save money in the long run

## Slide 3: Water Treatment Systems
Water treatment controllers
Chemical metering pumps
Bleed-off valve assemblies

## Slide 4: Water Treatment Controllers Probe Maintenance
Conductivity Probes
Without accurately controlling TDS levels, chemical treatment efforts are of little use
Inaccurate conductivity readings are caused by fouled/failed probes

## Slide 5: Conductivity Probe Maintenance
Clean probe vs. fouled probe
Some fouling only appears when the probe is dry...

## Slide 6: Conductivity Probe Maintenance
Loose coatings or oils - soft cloth with detergent
Hard coatings or scale
  mild acid (5% HCl)
  fine-grit sandpaper or emery cloth

## Slide 7: Conductivity Probe Maintenance
Always clean probe before calibration
> 5-10% error is excessive
Cleaning/calibration frequency depends on water quality (monthly is a good starting point)
Compare controller’s reading to calibrated hand tester (easiest) or check against buffer solutions

## Slide 8: Conductivity Probe Maintenance
Storage - wet or dry (drain sample line in winter to protect plastic piping from bursting)
Life span - several years when properly maintained

## Slide 9: pH/ORP Probe Maintenance
pH/ORP Probes
pH probes are required for automated acid feed programs
ORP probes are often used for automated oxidizing biocide feed
Probe anatomies are similar (reference junction & measurement surface)

## Slide 10: pH/ORP Probe Maintenance
Reference junction should be white
Soft coatings - vigorous stirring in water, squirt bottle, or gentle soft cloth
Hard coatings - mild acid (5% HCl)
Oils - Spray detergent (409)

## Slide 11: pH/ORP Probe Maintenance
pH probes should be cleaned & calibrated as needed (compare accuracy against a hand tester or standard solutions); weekly is a good starting point
Use periodic 2-point pH calibrations (low and high buffer solutions) to ensure accurate span
ORP is normally not calibrated (reads in a range, not a single point); clean probe if ORP doesn’t maintain the target Cl- or Br- residuals

## Slide 12: pH/ORP Probe Maintenance
Flat surface probes are self-cleaning to some degree (no dead spots)
Flat surface probes resist breakage (no protruding bulb)

## Slide 13: pH/ORP Probe Maintenance
pH/ORP probes last 6-24 months depending on quality of water; replace annually (or every other year at the longest)
New ORP probes take several hours to initialize and then respond within minutes
New pH probes are ready out of the box and respond in a matter of seconds
Reaction time and span accuracy decrease with age/fouling

## Slide 14: pH/ORP Probe Maintenance
Disconnect pH/ORP probes when the controller is unpowered (they are a type of battery that will drain)
pH/ORP probes cannot be stored dry
  4.0 buffer for pH probes (never DI water)
  tap water for ORP probes
Reviving a dried probe may be possible by soaking the probe in its storage solution for 8+ hours (save the shipping cap/bottle for storage)

## Slide 15: Flow Switch Maintenance
Flow switches prevent relay activation when the recirc pumps are off
Fouled flow switches lead to improper relay activation

## Slide 16: Flow Switch Maintenance
Thermal flow switches with no moving parts minimize debris hang-ups
Still susceptible to scaling over

## Slide 17: Metering Pump Maintenance
Pump maintenance is limited primarily to the liquid end.
A pump liquid end will last a few years under normal conditions.
Life span is affected by:
Chemical compatibility
Frequency of use
Temperature

## Slide 18: Metering Pump Maintenance
A typical pump liquid end consists of over 60 individual components arranged into major sub-assemblies.
Replacing assemblies vs. components:
  Less time consuming
  More cost effective

## Slide 19: Metering Pump Maintenance
Foot valve assembly
Foot valves feature an integral strainer screen and cartridge check valve.
Clean or replace when pump will not prime or when pump continually loses prime.
Install 1”-2” above bottom of tank to minimize blockages.

## Slide 20: Metering Pump Maintenance
Head assembly
Consists of head, suction & discharge valves, priming valve, diaphragm, & screws
Clean or replace when pump will not move chemical or when chronic leakage occurs.
Do not use Teflon tape on pump head fittings.
Tighten fittings only hand-tight.

## Slide 21: Metering Pump Maintenance
Injection valve assembly
Injection valves feature a spring-loaded cartridge check valve.
Clean or replace when chemical won’t pass or when tower water overcomes check valve.
Inspect nozzle tip for chemical crystallization and blockages.

## Slide 22: Metering Pump Maintenance
General tips:
Replace all wear & tear components at the same time (will save on multiple repair attempts).
Keep a spare liquid end on hand to prevent unnecessary downtime in chemical treatment program.
Inspect tubing annually for cracks and splits. Replace as needed.

## Slide 23: Bleed Valve Assemblies
Use a strainer with solenoid valves; clean as needed
Consider upgrading to a motorized ball valve if plugged valves are a recurring problem.

## Slide 24: Any Questions?